## Slide 1: CFD preliminary analysis Case study - Palazzo Ducale (Venice – Italy)
Task 3.3 Multi-physical environmental Simulations of CH Exhibition Impacts (M3; M32)

## Slide 2: Case study - Palazzo Ducale Room geometry
2 doors always open
5 persons
Lighting (5 sources)
8 m
9 m
6 m
HVAC system

## Slide 3: Case study - Palazzo Ducale Boundary conditions (summer’s day)
Inlet Mass Flow Rate = 0,14 Kg/s
T = 16,6 °C
UR = 91 %
Outlet:
0 Pa
T =26 °C
UR = 62 %
1 External wall (where there are HVAC inlet and outlet)
Q = 10.91 W/m2
The other walls are adiabatic
0 Pa
T = 26 °C
UR = 62%
Q = 70 W/m2 for person
Q = 10 W/m2 for unit
Ceiling
T 28 °C
Floor
T 28 °C

## Slide 4: Case study - Palazzo Ducale Temperature contour (K)

## Slide 5: Case study - Palazzo Ducale Velocity pathlines (m/s)
Front view
Side view